VNG25BS

1100kVA / 880kW

POWERED by CUMMINS

|  | DIESEL GENERATING SET | 400/230 V - 50 Hz - 3 Phase |
| --- | --- | --- |
|  |  | MODEL |  |  | VNG25BS |
|  |  | Standby | kVA |  | 25 |
|  | Power |  | kW |  | 20 |
|  | Pf. 0.8 | Prime | kVA |  | 22.7 |
|  |  |  | kW |  | 18 |

Standby: Continuous running at variable load for duration of an emergency. No overload is permitted on these ratings. In accordance with ISO 3046 .

Prime: Continuous running at variable load for unlimited periods with 10% overload available for 1 hour in any 12 hour period. In accordance with ISO 8528,ISO 3046.

- High quality, reliable and complete power unit

- Compact design

- Easy start and maintenance possibility

- Every generating set is subject to a comprehensive test program which includes full load testing, checking and provision of all control and safety shut down functions testing

- Fully engineered with a wide range of options and accessories: Canopy, sound proof canopy and on-road trailer

Manufacturer reserves the right to make changes in model, technical specifications, color, equipment and accessories without prior notice.

http://vietnhatpowers.com

ENGINE

|  |  | BAUDOUIN |  |  |
| --- | --- | --- | --- | --- |
|  | Model |  |  | 4M06G25/5 |
|  | Engine Power Output | kWm |  | 25 |
|  | at rated rpm | HP |  | 34 |
|  | Aspiration and Cooling |  |  | Turbocharged & Aftercooled |
|  | Total Displacement | Litre |  | 2.3 |
|  | No of Cylinders/ Valves |  |  | 4/8 |
|  | Engine Speed | rpm |  | 1500 |
|  | Bore and Stroke | mmxmm |  | 89 x 92 |
|  | Compression Ratio |  |  | 17.5:1 |
|  | Flywheel housing |  |  | SAE 4 |
|  | Fuel Consumption at full load | L/hr |  | 6.1 |
|  | Fuel Tank Capacity | Litre |  | N/A |
|  | Fuel System |  |  | Mechanical Pump |
|  | Coolant capacity | Litre |  | 3.6 |
|  | Governor |  |  | Electronic |
|  | Oil capacity Low / High (L) | Low/ High (L) |  | 7.1/9.5 |
|  | Exhaust flow @PRP (m3/ min) | m³/min |  | 5.32 |

Heavy duty Cummins diesel engine	Cooling radiator and fan

Four stroke, water cooled, turbocharged & aftercooled	Starter battery (with lead acid) including Rack and Cables

Direct injection fuel system	Flexible fuel connection hoses and manual oil sump drain valve

Electronic Governor system	Industrial capacity exhaust silencer and steel bellows

12/24 V D.C. starter and charge alternator	Jacket water heater(at automatic models)

Replaceable fuel filter, oil filter and dry element air filter	Operation manuals and circuit diagram documents

ALTERNATOR

| Design | Brushless single bearing, revolving field |  |
| --- | --- | --- |
| Stator | 2/3 pitch |  |
| Rotor | Single bearing, flexible disc |  |
| Insulation System | Class H |  |
| Standard Temperature Rise | 125 - 163°C Continuous |  |
| Exciter Type | Self Excited |  |
| Phase Rotation | A (U), B (V), C (W) |  |
| Alternator Cooling | Direct drive centrifugal blower fan |  |
| AC Waveform Total Harmonic Distortion | No load < 1.5%. Non distorting balanced linear load < 5% |  |
| Telephone Influence Factor (TIF) | <50 per NEMA MG1-22.43 |  |
| Telephone Harmonic Factor (THF) | <2% |  |
| Brushless, single bearing system, flexible disc, 4 poles | Impregnation with tropicalised epoxy varnish |
| Insulation class H | Solid state Automatic Voltage Regulator |
| Standard degree of protection IP21 (*IP22/IP23 is available.) | Stator winding with 2/3 pitch for improved harmonics |
| Self-exciting and self-regulating |  |  |

http://vietnhatpowers.com

DEEPSEA CONTROL SYSTEM

Control supervision and protection panel is mounted on the genset base frame.

The control panel is equipped as follows:

1. Auto Mains Failure Control Panel

Panel equipments:

- Control with AMF module

- Static battery charger

- Emergency stop push button

DSE 6120 MKIII

a) Generating set control module DSE6020 MKIII features:

- The module is used to monitor a mains supply and starts and stops a standby generating set

- Micro-processor based design

- Automatic control of mains and generator contactors

- Monitors engine performance and AC power output

- LED alarm indication

- Front panel configuration of timers and alarm trip points

- Easy push button control

STOP/RESET - MANUAL –TEST- AUTO – MUTE ALARM – START

b) Metering via LED display:

- Generator Volts (L-L / L-N)

- Engine oil pressure (PSI-Bar)

- Generator Ampere (L1,L2,L3)

- Engine temperature (°C&°F)

- Generator Frequency (Hz)

- Plant battery volts

- Engine hours run

- Mains Volts (Ph-Ph/Ph-N)

- Generator kVA, kWh

- Generator kW as % of rated kW setting

- Generator Cos (σ)

c) Alarms:

- Over and Under Speed

- Low and High Battery Volt.

- Start and Stop Failure

- Charge fail

- Over Current

- Under / Over Generator Voltage

- Low Oil Pressure

- Emergency stop

- High engine temperature

- kW overload

- Unbalanced load

- Independent earth fault trip

d) LED indications

Four configurable LED’s like:

- Mains available

- Generator available

- Mains on load

- Generator on load

2. Power Outlet Terminal Board Mounted on the Genset Base Frame

OPTIONAL EQUIPMENTS

Diesel Engine

- Oil heater

Alternator

- 3/4 Pole Output Circuit Breaker

- Anti-condensation Heater

Panel	Accessories

Charge ammeter	Bulk fuel tank

Transfer Switch 3 Pole	Automatic filling system

Transfer Switch 4 Pole	Fuel-water separator filter

Earth Fault ,single set	Low fuel level alarm

Residential silencer

Enclosure or sound proof canopy

Trailer

Manual oil drain pump

Tool kit for maintenance

http://vietnhatpowers.com

http://vietnhatpowers.com

CHASSIS

- The complete gen-set is mounted as whole on a heavy-duty fabricated, steel base frame

- Anti-vibration pads are fixed between the engine/ alternator feet and the base frame

- Base frame design incorporates an integral fuel tank (Up to 750 kVA)

- The generating set can be lifted or carefully pushed / pulled by the base frame

- Dial type fuel gauge and drain plug on the fuel tank

- Forklift pockets within base frame (up to 500kVA)

DIMENSIONS

OPEN TYPE

| DIMENSIONS (LxWxH) |  | mm |  | 1860*900*1381 |
| --- | --- | --- | --- | --- |
| DRY WEIGHT |  | kg |  | 960 |
|  | SOUND ATTENUATED TYPE |  |
| DIMENSIONS (LxWxH) |  | mm |  | 2494*963*1542 |
| DRY WEIGHT |  | kg |  | 1280 |

CANOPY

- All canopy parts are designed with modular principles

- Without welding assembly

- Doors on each side

- All metal canopy parts are painted by electrostatic polyester powder paint

- Exhaust silencer is protected against environment influences

- Thermally insulated engine exhaust system

- Emergency stop push button is installed outside of the canopy

- Easy lifting and moving

- Easy maintenance and operation

Viet Nhat Generator Joint Stock Company

Office : 3202-A2 An Binh City, 232 Pham Van Dong Street, Co Nhue ward 1, Bac Tu Liem District, Ha Noi City

Tel: 024.37958810           Fax: 024.37958809

Web:http://vietnhatpowers.com  Email:info@vietnhatpowers.com